Comprehensive Field Engineering Monograph

Volume 5: Petroleum Field Services – Diagnostic Detail and Operational Expertise

Prepared by: GPT-4o Expert Research Division
Industry Scope: Routine Service Operations, Component Replacement, and Regulatory Maintenance

### 1. Sump Sensor Replacement Protocol and Diagnostics

#### 1.1 Purpose and Compliance Function

- Detects presence of liquid in containment sump – water or product.

- Required by EPA 40 CFR §280.43(g) for leak detection in double-walled systems.

- Common brands: Veeder-Root, Franklin Fueling, Incon, Omntec.

#### 1.2 Removal and Replacement Procedure

- De-energize sensor circuit at ATG console.

- Use chemical-resistant gloves and isolate any flammable liquid.

- Unscrew or unclip sensor from mounting bracket; inspect for corrosion or float damage.

- Install new sensor with proper orientation (Veeder: arrows point down; Franklin: upright float).

- Test function by submerging in water and verifying alarm at console.

#### 1.3 Sensor Programming and Verification

- Use ATG console (e.g., TLS-450) to assign sensor zone.

- Log alarm response time; must register within 10 seconds of fluid contact.

- Record sensor serial and installation in compliance log.

### 2. Monthly Compliance Inspection

#### 2.1 Required Visual Checks

- Check for cracks or staining in spill buckets.

- Confirm tight fill caps, vapor caps, and shear valve integrity.

- Verify nozzle spouts, breakaways, and boot integrity.

- Ensure all warning labels are visible and not degraded.

#### 2.2 Documentation

- Use PEI RP900 checklist; must include technician initials, site ID, and date.

- Capture and archive photo evidence (e.g., sensors dry, buckets clean).

- Digital records should be backed up monthly and retained for 36 months.

#### 2.3 Failure Triggers

- Alarm or fluid presence in sumps.

- Cracked or compromised spill containment.

- Damaged sensors or disconnected harnesses.

### 3. Annual Line Leak Testing

#### 3.1 Test Methodology

- Must detect leak rate of 0.1 GPH at 150% of operating pressure.

- Test duration: Minimum of 1 hour for pressurized systems.

- Use certified 3rd-party test equipment (e.g., Leighton, LeakLogic, Tanknology).

#### 3.2 Procedure

- Isolate line and connect test manifold.

- Pressurize using inert nitrogen gas.

- Monitor pressure drop with digital gauge calibrated within last 12 months.

- Acceptable pressure decay: ≤3 psi over 1 hour.

#### 3.3 Documentation and Compliance

- Document test pressure, start and end time, technician license number.

- Submit report to site operator and AHJ if required.

- Store report alongside ATG history for audit trail.

### 4. POS System Upgrade

#### 4.1 Components Typically Upgraded

- Site controller (e.g., upgrade from Ruby Commander to Verifone Edge).

- Dispenser CRINDs (EMV, NFC-ready).

- Ethernet loop replacement with TCP/IP router.

#### 4.2 Upgrade Procedure

- Backup price book and configuration settings.

- Replace hardware one node at a time to avoid system-wide outages.

- Test network integrity with loopback and ping utilities.

- Reconfigure dispenser addresses and map to POS.

#### 4.3 Security and Compliance

- Must comply with PCI DSS 4.0.

- Install secure firmware (EMV L2 certified kernel).

- Verify anti-virus, TLS 1.2 encryption, and user authentication modules.

### 5. Shear Valve Trip Test

#### 5.1 Purpose and Mandate

- Verifies that shear (impact) valve closes upon dispenser impact.

- Required per NFPA 30A §6.6.4.

#### 5.2 Test Procedure

- Simulate impact using rated lateral force (typically 125–150 lbf).

- Verify poppet closure visually or with pressure drop test.

- Inspect for fuel seepage or delayed closure.

#### 5.3 Post-Test Validation

- Reseat valve and torque retaining bolts.

- Check for stem deflection, seal wear.

- Log test result, method, and tech signature.

Conclusion: These five services represent the backbone of operational reliability and regulatory compliance. This document provides the field-level procedures, diagnostics, and reporting practices for optimized execution and system integrity verification. Volume 6 will build on this with advanced system repair protocols and enhanced sensor calibration workflows.