Comprehensive Field Engineering Monograph

Volume 6: Advanced Maintenance & Calibration – Dispensers, Sensors, Overfill Prevention, and Chart Verification

Prepared by: GPT-4o Expert Research Division
Industry Scope: Equipment Calibration, Component Integrity, and UST Data Accuracy

### 1. Dispenser Flow Calibration and Meter Accuracy Verification

#### 1.1 Regulatory Calibration Standard

- Calibrate flow meters to ±6 cubic inches per 5-gallon draw (weights and measures standard).

- Ensure calibration seals remain intact or document resealing.

#### 1.2 Equipment and Procedure

- Use a certified 5-gallon prover can with volumetric certificate.

- Perform three consecutive test draws per product grade.

- Adjust meter calibration screw behind service door using appropriate tool (often Allen or torque driver).

- Post-adjustment, retest all grades and log volume discrepancies.

#### 1.3 Documentation

- Record initial and final readings, adjustment details, and tech ID.

- Submit calibration report to site operator and applicable weights & measures authority.

### 2. Overfill Prevention Valve (OPV) Inspection and Replacement

#### 2.1 Purpose and Function

- OPV (e.g., OPW 61SO, EBW 410) shuts off fuel delivery at 90–95% tank capacity.

- Required under EPA 40 CFR §280.20(c) for all new or upgraded systems.

#### 2.2 Inspection and Removal

- Access via drop tube inside tank; use OPV extraction tool or extension rod.

- Inspect float arm, seating gasket, and pivot mechanism.

- Replace if warped, corroded, or if float fails to rise and lock at target height.

#### 2.3 Reinstallation and Testing

- Seat new OPV with factory torque spec (usually 30–45 ft-lbs).

- Perform simulated fill using compressed air and dummy probe to trigger float lock.

- Document model, serial, and install date.

### 3. Sensor Calibration and Field Re-Verification

#### 3.1 ATG Sensor Types

- Common: Veeder-Root Mag Plus probes, brine sensors, interstitial sensors, discriminating cable.

- Calibration drift occurs due to float swelling, temp variation, or fluid contamination.

#### 3.2 Calibration Protocol

- Validate tank depth using tank chart and ATG stick readings.

- Pull probe, clean with isopropyl solution, and re-zero floats using OEM calibration cradle.

- Reinstall and run span test to ensure readings match known fluid level.

#### 3.3 Reporting

- Retain float calibration logs and float replacement date.

- Submit updated tank chart mapping if probe swap alters readings.

### 4. Vapor Line Repair and Leak Verification

#### 4.1 Line Types and Fail Points

- Typically flexible coaxial or dual-line with dry break fittings.

- Failures often occur at elbows, improperly torqued clamps, or degraded rubber gaskets.

#### 4.2 Leak Isolation Technique

- Use pressure decay test (CARB TP-201.3) with inert gas pressurization to 2.0” WC.

- Monitor for 0.05” WC drop in 5 minutes (pass/fail threshold).

- Apply soapy solution or ultrasonic sniffer to locate leak point.

#### 4.3 Repair and Retest

- Replace compromised segment using OEM-rated couplers.

- Retest entire system after repair and log retest values for audit.

### 5. Tank Chart Verification and Recalculation

#### 5.1 Purpose

- Tank chart accuracy ensures ATG volume conversion from inches to gallons is correct.

- Required to match calibration stick results within ±1%.

#### 5.2 Chart Development and Audit

- Measure tank dimensions manually: length, diameter, end-type (flat vs. hemispherical).

- Compare ATG readings with stick readings at ¼, ½, ¾, and full marks.

- Input into chart generation software (e.g., Veeder Chart Tool, AutoChart).

#### 5.3 Submission and Retention

- Save and back up revised tank chart with technician signature and date.

- Upload to ATG system and print physical copy for UST logbook.

Conclusion: Volume 6 expands the field technician’s toolkit with high-precision maintenance and calibration standards. These operations ensure accuracy, environmental safety, and regulatory integrity across core UST systems. Next up: vapor recovery diagnostics, turbine pump efficiency analysis, and sump integrity restoration.